PV panel bypass diodes

A single panel with a bad bypass diode can damage a panel when partial shading occurs.
All PV cells have some spot defects that has some level of shunt resistance. At normal forward conduction illuminated conditions the cell shunt resistance does not see greater than about 0.9v. But when partial shading occurs, the shaded cells will be reverse biased with higher voltage from other unshaded series connected cells. The cheaper the panel, the more likely it will be using PV cells with lower shunt resistance defects.
At a higher reverse bias voltage, due to shading, the cell's shunt defect resistance can get very hot. It can burn a hole in the plastic backing seal of panel, or damage the PV cell.

Bypass diodes are typically placed across every 18-26 series connected cells to limit shaded cell reverse bias on any single cell to less than 10-15 vdc.
Pellet packaged diodes are a poor choice for bypass diodes due to limited heat dissipation capability. When you have shading, the unshaded cells' current will be forced through the bypass diode. The bypass diode may have 6-10 amps of current with up to 0.5-0.8 volt diode voltage drop. This creates 3 to 8 watts of heating to diode. The diodes are also in a very hot ambient temp environment of sun heated panel, limiting their heat dissiplation. Pellet diodes will get very very hot, often damaging them.
Another dumb thing you will find on many cheap panels is two pellet, lower current rated diodes placed in parallel. Discrete diodes in parallel will not share the current equally.

------------------

Shorting across a panel will not damage it. (other than possible arcing damage to MC4 plug contacts) PV cells are illumination based current source. To PV cells it is not different than open circuit Voc. In both cases, any PV illumination generated electrical power is dissipated in cells. Since silicon PV cell are in the ballpark of 20% efficiency, their heating goes up by the 20% which is insignificant additional heating.

Two, not perfectly matched, and not thermally tightly coupled diodes in parallel will have one diode taking more of the current. Diode taking more of the current will get hotter, dropping its forward conduction voltage causing it to take more of the current, causing it to get even hotter.

Source:
https://diysolarforum.com/threads/diode-replacement-in-junction-box.68361/post-864448