## AC Systems
| Applicant: | N/A |  |  |  | Date: | N/A
| Host Customer: | N/A
Instructions: | This spreadsheet calculates the battery energy capacity, total inverter output and system rated capacity of AC energy storage systems applying to the Self-Generating Incentive Program for incentives. Applicants must provide documentation supporting all inputs including but not limited to amp-hour capacity of each battery, number of batteries, system voltage, discharge duration, continuous power output of inverter, CEC inverter efficiency and number of inverters. See the 2017 SGIP Handbook for details of eligibility and documentation requirements. All yellow cells must be completed by Applicant/Host Customer.
Amp-Hour Capacity of Each Battery = |  |  | 56.624 | Ah | Amp hour rating of each battery based on the expected depth of discharge at the design duration of discharge
Number of Batteries = |  |  | 1 |  | Total number of batteries in the system
Nominal Battery Voltage = |  |  | 280.8 | Volt DC | Nominal battery voltage
Discharge Duration = |  |  | 2.29 | Hours | Design discharge duration based upon use case and spec sheet information
Continuous Power Output of Inverter = |  |  | 7.6 | kVA | Continuous as opposed to maximum power output of inverter
CEC Inverter Efficiency = |  |  | 96.5% | percent | CEC rated inverter efficiency as found on gosolar website
Number of Inverters = |  |  | 1 |  | Total number of inverters in the system
Total Energy Storage Capacity (kWh AC) = |  |  | 15.3435 | To be entered into SGIP Application
|  | = | Amp-hour Rating x No. of Batteries x Nominal Battery Voltage x CEC Inverter Efficiency / 1000
Total Inverter Output (kW AC) = |  |  | 7.6 |  |  |  |  | Renewable
|  | = | Continuous Power Output of Inverter x No. of Inverters |  |  |  |  | Grid
Total Rated Capacity (kW AC) = |  |  | 6.7002 | To be entered into SGIP Application
|  | = | Lesser of Total Inverter Output and Battery Energy Capacity / Discharge Duration

## DC Systems
| Applicant: |  |  |  |  | Date:
Host Customer:
Instructions: | This spreadsheet calculates the battery energy capacity, total inverter output and system rated capacity of DC energy storage systems applying to the Self-Generating Incentive Program for incentives. Applicants must provide documentation supporting all inputs including but not limited to amp-hour capacity of each battery, number of batteries, system voltage, discharge duration, continuous power output of DC-DC converter, DC-DC converter efficiency and number of DC-DC converters. See the 2017 SGIP Handbook for details of eligibility and documentation requirements. All yellow cells must be completed by Applicant/Host Customer.
Amp-Hour Capacity of Each Battery = |  |  |  | Ah | Amp hour rating of each battery based on the expected depth of discharge at the design duration of discharge
Number of Batteries = |  |  |  |  | Total number of batteries in the system
Nominal Battery Voltage = |  |  |  | Volt DC | Nominal battery voltage
Discharge Duration = |  |  |  | Hours | Design discharge duration based upon use case and spec sheet information
Continuous Power Output of DC-DC Converter = |  |  |  | kVA | Continuous as opposed to maximum power output of DC-DC converter
DC-DC Converter Efficiency = |  |  |  | percent | Efficiency of DC-DC converter
Number of DC-DC Converters = |  |  |  |  | Total number of DC-DC converters in the system
Total Energy Storage Capacity (kWh DC) = |  |  | 0 | To be entered into SGIP Application
|  | = | Amp-hour Rating x No. of Batteries x Nominal Battery Voltage x DC-DC Converter Efficiency / 1000
Total DC-DC Converter Output (kW DC) = |  |  | 0
|  | = | Continuous Power Output of DC-DC Converter x No. of DC-DC Converters
Total Rated Capacity (kW DC) = |  |  | #DIV/0! | To be entered into SGIP Application
|  | = | Lesser of Total DC-DC Converter Output and Battery Energy Capacity / Discharge Duration